## VIPA GmbH 13.11.2001

## Profibus Slave VIPA 253-2DP50

## Redundancy Mode

The VIPA 253-2DP50 only supports system redundancy.

The first PROFIBUS channel who is in state DataExchange is the primary slave, the other is the backup slave.

The primary slave uses the cyclic communication to send and receive the process values. The backup slave also send and receive the process values, but inside the slave the send data will be ignored.

If the slave redundancy enhancements detect a communication error to the primary master, the slave make a switch over to the backup slave.

You can also make a switch over to the other slave by stopping the master.

With the redundancy state diagnostic telegram the master will be informed of all changes inside the slave.

Redundancy state diagnosis

| # Byte |  |  |
| --- | --- | --- |
| X | Header | 0x08 |
| X+1 | Status Type | 0x80 |
| X+2 | Reserved | 0x00 |
| X+3 | Reserved | 0x00 |
| X+4 | Reserved | 0x00 |
| X+5 | Red_State |  |
| X+6 | Red_State from other Slave Device |  |
| X+7 | Reserved | 0x00 |

## Red_State:

| # Bit | Meaning |
| --- | --- |
| 0 | Slave is Backup Slave |
| 1 | Slave is Primary Slave |
| 2 | Reserved |
| 3 | Reserved |
| 4 | Slave is in DataExchange |
| 5 | Reserved |
| 6 | Reserved |
| 7 | Reserved |

Over the GSD-File you are allowed to disable the diagnostic messages.

Diagnostic: enable/disable all diagnostic messages

Redundancy diagnostic: enable/disable the redundancy state diagnostic messages

Additional Feature: With the module "Statusbyte IM253-2DP50" (two bytes) inside the GSD-File you can put the "Red-State byte" and the "Red State byte from the other Slave" directly to the process input area.

But notice: This module must be the last module in the configuration!

## Parameterization:

Only that station who is the first in DataExchange can parameterizise the analogue modules.  If you want to change the parameters of the analogue modules, both channels must go to the state WaitPrm and then only the first channel who is in DataExchange can parameterizise the modules.

GSD-File: DP2v550.gsd System 200

## System characteristic

- Power supply of connected System 200V modules with up to 3A

- Power down recognition at 8.5V

- Maximum of 152 byte Input and 152 byte Output data

- Maximum of 237 byte parameter data

- Maximum of 64 byte diagnostic data

- Supports all Profibus data rates

- Possible Profibus addresses are 1..126  (A startup with address 0 is not valid because it is reserved for a Profibus master. In that case the LED indicators RDY and ERR are flashing together.) After a startup with a valid Profibus address, slaves with address switches can execute two special functions:

- After a startup with System 200V modules connected, changing to address 00 causes a single flash store operation of the internal diagnostics buffer.

- After a startup without modules connected, the EEPROM and the internal diagnostic data in flash is cleared. When finished, the RDY LED lights up and the slave is halted.

## LED Indicators

| # Designate |  | Colour | Meaning |
| --- | --- | --- | --- |
| PW | Power | Yellow | Lights up, when power supply is alright. |
| ER | Error | Red | Lights up for a short time at startup (=power up). Is switched on when a internal error occured. Flashes if an initialization error happened (e.g. unknown module detected) Flashes alternately with RD when received wrong configuration data. Flashes together with RD when a parameterization error happened. (e.g. you sent parameter data to a nonconfigurable modules like a digital module) |
| RD | Ready | Green | Flashes after self test and initialization procedure are passed with OK. |
| DE | Data Exchange | Yellow | Is switched on in state Data Exchange, which means that a connection with the Profibus master has been established and IO Data is exchanged. |

## Redundancy Mode LED Indicators

| # Designate |  | Colour | Meaning |
| --- | --- | --- | --- |
| RD;DE | Ready, Data Exchange | Green, Yellow | Both LED on, the PROFIBUS channel is the active one (read, write to the backplane). |
| RD;DE | Ready, Data Exchange | Green, Yellow | RDY off and DE on, the PROFIBUS channel is the passive one (only read from the backplane). |

## Diagnose Structure

| # Byte |  |  |
| --- | --- | --- |
| 0 | Profibus Norm Diagnostics, see VIPA manual |  |
| 1 |  |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
| 5 |  |  |
| 6 | Header for vendor specific Diagnostics |  |
| 7 | Message type | Hex, Dez, Message 0A = 10: DP-parameterization error 14 = 20: DP-configuration length error 15 = 21: DP-configuration entry error 1E = 30: power fail / power off 28 = 40: VBUS-parameterization error 29 = 41: VBUS-initialization error 2A = 42: VBUS-bus error 2B = 43: VBUS-read/write error (=Quittungsverzug) 32 = 50: diagnostics alert of a System 200 module 33 = 51: process alert of a System 200 module 3C = 60: New DP address was set 3D = 61: Slave entered state READY 3E = 62: Slave entered state DATA_EXCHANGE |
| 8 | Slot (=module number) | 1 to 32 |
| 9-29 | Additional information to 7 | (see following tables) |

DP-parameterization error (Message type: 0Ahex  = 10dez )

This diagnostic message is created of the parameter telegram is too short  or too long.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 7 |
| 7 | Message type | 10 |
| 8 | Modulnummer, Steckplatz (1..32) | 0 |
| 9 | Length of user parameter data |  |
| 10 | S7-Mode | 0 : Standard mode 1 : S7-400 Special Mode |
| 11 | Number of Digital modules (Slave) |  |
| 12 | Number of Analog modules (Slave) |  |
| 13 | Number of Analog modules (Master) |  |

DP-configuration length error  (Message type: 14hex = 20dez)

The length of the configuration telegram is compared with the recognized modules on the vbus.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 6 |
| 7 | Message type | 20 |
| 8 | Slot number (1..32) | 0 |
| 9 | Number of configuration bytes (Master) |  |
| 10 | Number of configuration bytes (Slave) |  |
| 11 | S7-Mode | 0 : Standard mode 1 : S7-400 Special Mode |

DP-configuration entry error (Message type: 15hex = 21dez )

The configuration bytes, sent from from master, are compared with the configuration bytes which are created by the slaves depending on the attached System 200V modules.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 6 |
| 7 | Message type | 21 |
| 8 | Slot number (1..32) |  |
| 9 | Configuration byte (Master) |  |
| 10 | Configuration byte (Slave) |  |
| 11 | S7-Mode | 0 : Standard mode 1 : S7-400 Special Mode |

VBUS-Parameterization error (Message type: 28hex = 40dez)

Sending Parameters to slot number x was not successfull.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 3 |
| 7 | Message type | 40 |
| 8 | Slot number (1..32) |  |

VBUS-Initialization error (Message type: 29hex = 41dez )

Internal Error at initialization or a unknown module was recognized on VBUS.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 2 |
| 7 | Message type | 41 |

VBUS-Bus error (Message type: 2Ahex = 42dez)

Hardware error or module dropout.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 2 |
| 7 | Message type | 42 |

VBUS-Read/Write error (=Quittungsverzug) (Message type 2Bhex = 43dez)

An error happened in a read or write-operation.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 3 |
| 7 | Message type | 43 |
| 8 | Slot number (1..32) (255 = unknown) |  |

Diagnostics alert of a System 200V module (Message type 32hex = 50dez)

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 19 |
| 7 | Message type | 50 |
| 8 | Slot number (1..32) |  |
| 9..21 | Diagnostic data of the System 200V module (see manual) |  |

Process alert of a System 200V module (Message type 33hex = 51dez)

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 19 |
| 7 | Message type | 51 |
| 8 | Slot number (1..32) |  |
| 9..21 | Process alert data of the System 200V module (see manual) |  |

New DP address was set (Message type: 3Chex = 60dez )

After acceptance of the service ‘Set Slave Address’ the slave sends the following diagnosis message and reboots. Then the slave is active on network with his new address!.

| # Byte |  |  |
| --- | --- | --- |
| 0..5 | Profibus Norm Diagnostics see VIPA manual |  |
| 6 | Length of diagnostic data | 2 |
| 7 | Message type | 60 |